## Modbus TCP Interface V1.00
Energise CRIO Modbus Register Map | V2.0
2019-10-04
Author: Daniel Sandez
Customer: Energise Project
Notes:
- Element is the Modbus master
- BESS is a Modbus slave
- Master has a heartbeat used to determine communication status
- Initial communications are established by the Element updating heartbeat to the slave, putting system in remote mode
- If Element heartbeat remains static for more than 30s, system will go to idle and local mode
-IP address: TBD, Port :502
Read/Write Registers
Variable | Modbus Register | Bit Offset | Value Type | MIN | MAX | FACTOR | Number of Bits | Unit | Value Table | Update Time | Access Permissions | Comment
ElementHeartbeat | 1 | 0 | Unsigned Integer | 0 | 65535 | 1 | 16 | NA | NA | 100ms | rw | Increments by 1 every 100ms
InverterEnable | 11 | 0 | Unsigned Integer | 0 | 1 | 1 | 16 | NA | NA |  | rw | 0 = Idle, 1 = Active
ActivePowerCmd | 12 | 0 | Signed Integer | -150 | 150 | 0.01 | 16 | kW | NA |  | rw
ReactivePowerCmd | 13 | 0 | Signed Integer | -150 | 150 | 0.01 | 16 | kVar | NA |  | rw
Read Only Registers
Variable | Modbus Register | Bit Offset | Value Type | MIN | MAX | FACTOR | Number of Bits | Unit | Value Table | Update Time | Access Permissions | Comment
SOC | 1 | 0 | Unsigned Integer | 0 | 100 | 0.5 | 16 | % | NA |  | r | Reported by BMS
ErrorStatus | 11 | 0 | Unsigned Integer | 0 | 255 | 1 | 16 | NA | ErrorStatus |  | r | Generated in cRIO
ControlMode | 12 | 0 | Unsigned Integer | 0 | 1 | 1 | 16 | NA | NA |  | r | 0 = Local, 1 = Remote
ActivePower | 21 | 0 | Signed Integer | -320 | 320 | 0.01 | 16 | kW | NA |  | r | Reported by inverter
ReactivePower | 22 | 0 | Signed Integer | -320 | 320 | 0.01 | 16 | kVar | NA |  | r | Reported by inverter
PowerFactor | 23 | 0 | Signed Integer | -1 | 1 | 0.01 | 16 | NA | NA |  | r | Calculated from inverter
GridACVoltageAB | 24 | 0 | Unsigned Integer | 0 | 3200 | 0.1 | 16 | VAC | NA |  | r | Reported by inverter
GridACVoltageBC | 25 | 0 | Unsigned Integer | 0 | 3200 | 0.1 | 16 | VAC | NA |  | r | Reported by inverter
GridACVoltageCA | 26 | 0 | Unsigned Integer | 0 | 3200 | 0.1 | 16 | VAC | NA |  | r | Reported by inverter
InverterStatus | 31 | 0 | Unsigned Integer | - | - | 1 | 16 | NA | InverterStatus |  | r | Reported by inverter
Begin Value Tables
Value Table | Enumeration Value | Description |  | Comment
ErrorStatus | 0 | No Error
ErrorStatus | 1 | SOC Too High |  | Maximum SOC reached. Only discharge is allowed. Discharge to clear error.
ErrorStatus | 2 | SOC Too Low |  | Minimum SOC reached. Only charge is allowed. Charge to clear error.
ErrorStatus | 3 | Cell Voltage Too High |  | Maximum cell voltage reached. Only discharge is allowed. Discharge to clear error.
ErrorStatus | 4 | Cell Voltage Too Low |  | Minimum cell voltage reached. Only charge is allowed. Charge to clear error.
ErrorStatus | 5 | Cell Temperature Too High |  | Maximum cell temperature reached. Intervention required.
ErrorStatus | 6 | Cell Temperature Fault |  | A temperature sensor has failed. Intervention required.
ErrorStatus | 7 | BMS Signal Lost |  | CAN communication with BMS has failed. Intervention required.
ErrorStatus | 8 | Inverter Signal Lost |  | Modbus communication with inverter has failed. Intervention required.
ErrorStatus | 9 | BMS and Inverter Signal Lost |  | Both CAN and Modbus communication have failed. Intervention required.
InverterStatus | 0 | Idle
InverterStatus | 1 | Active |  | Inverter is enabled.
InverterStatus | 2 | Tripped |  | A fault has been triggered. Intervention required.
End Value Tables